Form G5-1

|  | PG&E LOG | 19H051 |
| --- | --- | --- |
|  | WO/GM |  |
|  | D&C |  |

PACIFIC GAS AND ELECTRIC COMPANY

GENERATION PRE-PARALLEL INSPECTION

| Name of Project: | R.W. Matthews Dam Hydroelectric Plant |
| --- | --- |
| Location: | 40 Lower West Side Road, Ruth, CA 95526 |

| Transmission Line No. |  |  | Distribution Circuit No. |  |
| --- | --- | --- | --- | --- |

| 1. | Maintenance Data: |
| --- | --- |

| Generation Customer’s Maintenance Chief | Dale Davidsen |
| --- | --- |
| Telephone Number | 707-822-2918 |
| Generation Customer’s Regular Maintenance Interval | Annual maintenance, Triannual relay testing |
| Electrical Contractor | n/a |

| 2. | Test Reports Attached: | Yes |  |  | No |  |
| --- | --- | --- | --- | --- | --- | --- |

| If not, who has the reports: |  |
| --- | --- |

| 3. | Generation Facility Manual Disconnect Device for PG&E Line Clearances: |
| --- | --- |

| Manufacturer |  |
| --- | --- |
| Model Number |  |
| PG&E Device Number |  |

| 4. | Designated PG&E Electric Control Center | Name & Desk Phone # |
| --- | --- | --- |

| 5. | PG&E Inspector |  |
| --- | --- | --- |
|  | NAME | PHONE NO. |

| Date Inspection Performed: |  |
| --- | --- |
| Date Facility Placed on 30 Day Test Released: |  |

Distribution:

PG&E Designated Electric Control Center (1)

Division Project Coordinator (1)

Marketing Services (1)

Power Contracts (1)

GM&C Area Engineering (1)

System Dispatch (1)

| Form G5-1 |  |
| --- | --- |
| (Continued) | PG&E LOG | 19H051 |
|  | WO/GM |  |
|  | D&C |  |

PACIFIC GAS AND ELECTRIC COMPANY

GENERATION PRE-PARALLEL INSPECTION

| 1a. | Generator Nameplate: | 1000 | kW | 4160 | Volts |  | Pf |  | 1( | X | 3( |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| b. | Generator Type: | Synchronizing: | Connection: |
| --- | --- | --- | --- |
| X | Synchronous |  | X | Auto |  | X | WYE-Ground |
|  | Induction |  |  | Manual w/ Relay |  |  | WYE-Ungrounded |
|  | DC w/ Inverter |  |  |  |  |  | Delta |

| Manufacturer | Ideal Electric Company |  | Serial No. |  |
| --- | --- | --- | --- | --- |

| c. | Generator Prime Mover: |  |  |
| --- | --- | --- | --- |

| Wind |  | Water | X | Steam |  | Solar |  | Fuel Cell |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Other, specify |  |
| --- | --- |

| d. | Generator Breaker or Contactor: |
| --- | --- |

| Manufacturer | Siemens-Allis |  | Serial No. |  |
| --- | --- | --- | --- | --- |

Model # MA-250-1200

|  | Thermal/Magnetic Overcurrent |
| --- | --- |
|  | Undervoltage Release (optional under 40kW) |
| x | DC Shunt Trip (required over 40kW) w/battery ___X_____ Capacitor Trip _______ |
| 125 | Control Voltage (Not acceptable for use) |

| 2. | Dedicated Transformer: | Yes | X | 3( | X | 1( |  | 3-1( |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | No |  | Bank of 3-1( |  |  |

| Customer owned | X |  | PG&E owned |  |
| --- | --- | --- | --- | --- |
| Bank Rating: |  | 2000 | KVA Transformer |  | % |  | MVA Base |

| Transformer Connection: | Primary | 12,470 | volts |
| --- | --- | --- | --- |
|  | Secondary | 4,160 | volts |

| Protected by: |  | Fuse Size | Type RBA |  | Amps | 150 |  | Other |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 3. | Ground Protection Required: |  | Yes |  |  | No |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

| If Yes, type of ground detection (check type): |
| --- |
|  | Ground Bank with overcurrent relay. |
|  | Broken Delta Ground Bank with low pick up overvoltage relay. |
|  | Ground Overcurrent relay in neutral or dedicated transformer. |
|  | Low voltage pick up overvoltage relay in elevated neutral of dedicated transformer. |
|  | Other |  |

Form G5-1

GENERATION PRE-PARALLEL INSPECTION

PROTECTIVE DEVICES:

| RELAY | Standard Device Number | Required Yes/No | Mfr and Model | Settings | Specific Breaker Tripped | Date of Function Test | PG&E Inspector Initials |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Zone 1 Distance | 21Z1 | NO | N/A |  |  |  |  |
| Zone 2 Distance | 21Z2 | NO | N/A |  |  |  |  |
| Directional Phase O.C. | 67 | NO | N/A |  |  |  |  |
| Directional Ground O.C. | 67N | NO | N/A |  |  |  |  |
| Non-directional O.C. | 50/51 | NO | N/A |  |  |  |  |
| Ground or Neutral O.C. | 50/51N | NO | N/A |  |  |  |  |
| Overvoltage Ground | 59N | NO | BE 1 59N BE1-59N A5E E2CA0N0 | 20V, 1 sec (there are also units on each gen 9.6V, .04 sec) |  | 11/29/12 |  |
| Overcurrent with voltage restraint | 51V | NO | GE IJF51A1A | 8A @ 100% restraint, 2A @0 restraint TD=5 Applied on each Gen | Gen 1, Gen 2 | 11/29/12 |  |
| Underfrequency | 81U | NO | e-max Type 707D04S PUD digital | 54 Hz, 15 Cycles | Main | 11/29/12 |  |
| Overfrequency | 81O | NO | GE JF51A1A | 64 Hz | Main | 11/29/12 |  |
| Synchronizing | 25 | YES | BE1-25A Style A1F5V3D1 New, replacing old unit | Sync angle 0 slip- 0 deg Advanced Angle- 4 Delta V Gen Low- 3 Delta V Gen High- 3 Gen UV- 110 Slip Freq- .1 Hz | ALL OK Settings verified in relay display See Note | Bench test to be 9/23/15 | 12/2/2015 DWGd Function test all OK |
| Auto Synchronizing | 15/25 | YES | Same as above | Same as above | Same as above | Same as above | Same as above |
| Undervoltage | 27 | NO | BE1-27 A3G | 105.5V 3.25 Cy | Main | 11/29/12 |  |
| Overvoltage | 59 | NO | GE PJV | 144V inst | Gen 1, Gen 2 | 11/29/12 |  |
| Transfer Trip From: |  |  |  |  |
| Transfer Trip From: |  |  |  |  |
| Reclose Block at: |  |  |  |  |
| Reclose Block at: |  |  |  |  |

GENERATORS OPERATION:

| (A). | Verify operation of the generator(s) at 0.90 P.F. lag and at 0.95 P.F. lead while delivering rated output: PG&E inspector initials | N/A |
| --- | --- | --- |
| (B). | Verify operation of the generator(s) at 1.05 per unit voltage while delivering rated output: PG&E inspector initials | N/A |

Note: this relay is set via the front panel controls – there is no setting file to download/upload.